- Identify the chemicals in use in each work location and review the MSDS materials for advice about the risk of eye injury if the product is splashed into the eye.

  - Install a plumbed eye wash if the product is identified as a “corrosive substance” which OSHA would define as: “A chemical that causes visible destruction of, or irreversible alterations in, living tissue by chemical action at the site of contact. For example, a chemical is considered to be corrosive if, when tested on the intact skin of albino rabbits by the method described by the U.S. Department of Transportation in appendix A to 49 CFR part 173, it destroys or changes irreversibly the structure of the tissue at the site of contact following an exposure period of four hours”.

- Non corrosive, but irritating chemicals can be evaluated using the risk assessment tool.

  - Evaluate the relative risk, for example pouring from one container to another, vs using a wipe that contains the chemical. High risk gets 3 points; low risk gets 1 point.

  - Evaluate the relative risk based on hospital experience, your incident reporting system and the professional literature. Assign 3 points if you have reports and the literature reports this being a problem, assign 2 points if you have never experienced a problem and there is only one or very few reports in the literature. Assign 1 point if you have never experienced a problem and there are no reports in the literature.

  - Evaluate the inherent staff mitigating factors such as staff always wearing PPE and eye protection. Assign 1 point if PPE and eye protection is available and staff routinely where it. Assign 2 points if eye protection is not available or not used.

  - Evaluate staff preparation, or ability of staff to assist each other. If there is a splash, can staff guide, aid their coworker to a plumbed eyewash? Assign 1 point if there are always staff to assist, and 2 points if the worker is alone in this area.

  - Evaluate how long it would take to get to a plumbed eyewash if needed. Assign 3 points if longer than 30 seconds, 1 point if less than 10 seconds, 2 points between 10 and 30 seconds.

- The tool will total your scores for each location evaluated. Your hospital can assign a threshold, above which you will install plumbed eye wash stations and below which you may have none or use bottle eyewash along with assistance to a plumbed eyewash. The worst possible score is 13, the best possible score is 5.