| Passed? Y/N | Nurses Station & Hallways Staff Assignment #1 | Call to Fix/correct: |
| --- | --- | --- |
|  | Exit doors, smoke and fire doors - Exit door not blocked - Exit door not locked - Nothing in the swing path of a magnetically held open door - No wood wedges or other devices to prop doors - Close properly and latch - Doors to hazardous areas are labeled as such and locked - No gap >1/8 inch between closed doors - No undercut >¾ inch between door and floor - Fire door rating label is readable, not painted over Hallways & stairways - Free of clutter and storage – 8 feet unobstructed - Carts on wheels not parked for >30 minutes - Isolation carts and crash carts are considered “in use”, are OK - Exits signs fully illuminated and visible Fire alarm pull stations - Accessible, not blocked Evacuation route maps - Posted and accurate Fire extinguishers - Not blocked - Inspected monthly - Inspection tag has initials, month/day/year recorded Ceiling tiles - Are in place and clean - Not cracked, wet or stained Sprinkler heads - 18” clearance under sprinkler heads - Nothing attached to them - Not bent or rusted, the ring is flush with ceiling Hand Sanitizer - Not empty - Not installed over or near light switches, electric outlets Walls, ceilings - In good repair - No damage or holes Check bulletin boards - No patient specific information, no damaging information, no outdated information (remove any violations) | X____ X____ X____ X____ X____ X---- X____ X____ X____ X____ |

|  | Medical Equipment - Equipment is approved for use, tagged per policy - PMs up to date - Clean and dirty stored separately - Out of service equipment is labeled as such - Medical equipment is cleaned per policy Under sink storage - Clear of unapproved items (discard or properly store items) Glucometers - Cleaned between each use - Test strips are dated when open, they expire 90 days after opening - Test solution is not expired - Discard anything outdate, not labeled Medical gas shutoff - Valves clearly marked with room number - Not blocked - Staff can describe who can shut these off and when Medical gas alarm panels - Working properly, not obstructed Crash cart - Checks done per policy, documented - Contains listed equipment and meds - Defib pads and meds are not expired - Batteries in the laryngoscope handle not expired - Ensure the defib is plugged in when stored & unplugged when tested - (Notify charge nurse if any failure) Electric panel locked and not obstructed Electric outlets/switch plates/cords in good condition Furniture, wheel chairs, vinyl-covered mattresses/carts - Not ripped or cracked - No holes, cleaned per policy ID badges worn by all employees Patient specific information - Not visible/available - Computers are locked when unattended | X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ |
| --- | --- | --- |
|  | Hazardous materials properly stored/labeled Waste receptacles emptied before overfilled Sharps containers - Are secured/not overfilled - Mounted below 4’10” - Call Housekeeping to empty (X____) Doors to Biohazard areas are kept closed, labeled Disinfectants/chemicals - Include manufacturer warning labels, - Not passed expiration date - Stored away from danger or children, etc - SDS sheets accessible, up to date Trash bins not overflowing (call housekeeping X____) O2 tanks - Stored in approved storage - No O2 left standing on the floor - Empty tanks should be replaced - (call Respiratory Therapy for issues xxxx) | X____ X____ X____ X____ X____ X____ X____ |

| Passed? Y/N | Medication Room Staff Assignment #2 | Who to call to fix/correct: |
| --- | --- | --- |
|  | Door to Med Room - Locked, per policy - Door not “propped” open, lock not taped over - Combination for lock not posted near door - Key for meds not stored near the locked meds Check all drawers and cabinets for expired, unnecessary stuff. IV Pumps - PMs up to date - Cleaned per policy Refrigerators/freezers - Temperature logs complete - Action is noted on out of range values No pre-labeled/unfilled syringes Look alike-sound alike meds - Stored per policy (stickers, separated, etc) - LASA list is posted or readily available - Staff can speak to IV Bags - Check for expiration date - Ensure bags are not spiked prior to use, per policy - Clean IV pumps must be covered and plugged in Multi-dose vials - Labeled with the beyond use date or the date they are to expire - Not kept for reuse if opened and used in a patient care area - No opened single dose vials kept for reuse - Expire 28 days after opening - no medications are expired. Ceiling tiles - Are in place and clean - Not cracked, wet or stained Sprinkler heads - 18” clearance under sprinkler heads - Not bent or rusted, the ring is flush with ceiling Hand Sanitizer - Not empty Walls, ceilings - In good repair, No damage or holes Sharps containers - Are secured/not overfilled Under sink storage - Clear of unapproved items (discard or properly store items) | X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ |

| Passed? Y/N | Dirty and Clean Utility Room Staff Assignment #3 | Who to call to fix/correct: |
| --- | --- | --- |
|  | Door - Closed, and/or locked if required, No door stopper Check all drawers and cabinets for expired, unnecessary stuff. Eyewash Station - Testing done per policy & documented Waived Testing Supplies - Ensure test strips are dated when open, per policy, not expired Linen and Trash Chute - Doors close tight and latch, door locked if policy - Not accessible to children, confused patients PPE - Readily available and used when required Cardboard shipping boxes not stored on floor Red Liner containers - Must be covered, not overflowing (X____) Blood Collection Tubes - Checked for expiration dates, discard outdated supplies Clean Linen Cart - Covered at all times, no exposed clean linen - Linen cart has hard bottom, not wire open bottom O2 tanks - Stored in approved storage - Full stored separate from partial or empty - No O2 left standing on the floor - Empty tanks should be replaced - (call Respiratory Therapy for issues xxxx) Ceiling tiles - Are in place and clean Not cracked, wet or stained Sprinkler heads - 18” clearance under sprinkler heads - Not bent or rusted, the ring is flush with ceiling Walls, ceilings - In good repair, No damage or holes Medical Equipment - PMs up to date - Clean and dirty stored separately - Out of service equipment is labeled as such - Medical equipment is cleaned per policy Soiled equipment & linen separated from clean | X___ X____ X____ X___ X X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ |
| Passed? Y/N | Dirty and Clean Utility Room, Continued Staff Assignment #3 | Passed? Y/N |
|  | Hazardous materials properly stored/labeled. Waste receptacles emptied before overfilled. Sharps containers - Are secured/not overfilled. - Mounted below 4’10” - Call Housekeeping to empty (X____) Doors to Biohazard areas are kept closed, labeled. Disinfectants/chemicals - Include manufacturer warning labels, - Not passed expiration date - Stored away from danger or children, etc - SDS sheets accessible, up to date Trash bins not overflowing (call housekeeping X____) Under sink storage - Clear of unapproved items (discard or properly store items) Sharps containers - Are secured/not overfilled. | X____ X____ X____ X____ X____ X____ X____ X____ |

| Passed? Y/N | Kitchen or Pantry Staff Assignment #4 | Who to call to fix/correct: |
| --- | --- | --- |
|  | Door - Closed, No door stopper Food refrigerator - Temperature monitoring complete, recorded - Out of range temperatures have action noted in log - Food is prepackaged or labeled for individual patients - Patient food brought from home is labeled/dated - There is some schedule for discarding open products, cleaning - No expired food, discard undated and outdated - It is clean - No staff food stored - Bottom shelve is solid, to protect food Meal trays and patient specific snacks - Have two patient identifiers Counters - Are clean Microwave - Is clean Ice Machine - No mold behind machine, clean (call X____) Under sink storage - Clear of unapproved items (discard or properly store items) Check all drawers and cabinets for expired, unnecessary stuff. Ceiling tiles - Are in place and clean - Not cracked, wet or stained Sprinkler heads - 18” clearance under sprinkler heads - Not bent or rusted, the ring is flush with ceiling Walls, ceilings - In good repair, No damage or holes | X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ X____ |